## System Specifications
22 kWp PV System — Technical Specifications & Performance
Parameter | Value | Notes
📍 Site & Weather
Location | Kömürcüler, Antalya, Turkey
Latitude | 37.07 °N
Longitude | 30.62 °E
Altitude | 297 m | PVsyst report p.2
Time Zone | UTC+3
Weather Data | Meteonorm 8.2 (2003–2013) | PVsyst report p.2
Albedo | 0.2
⚡ PV Array
PV Module Model | TSM-DE19-550
Module Manufacturer | Trina Solar (Generic in PVsyst)
Module Power (Wp) | 550
Number of Modules | 40
Array Configuration | 4 strings × 10 modules
Total DC Power (kWp) | 22
PV Tilt / Azimuth | 7° / 0° (South-facing)
PV Surface Area (m²) | 105
STC Efficiency (%) | 21.05 | PVsyst loss diagram
🔌 Inverter
Inverter Model | SUN2000-20KTL-M2
Inverter Manufacturer | Huawei (Generic in PVsyst)
Inverter Power (kWac) | 20
Number of Inverters | 1
DC/AC Ratio | 1.1
Operating Voltage (V) | 160 – 950
📊 Performance Results
Produced Energy (kWh/year) | 31613 | PVsyst E_Grid, report p.2
Specific Production (kWh/kWp/year) | 1437 | PVsyst report p.2
Performance Ratio (%) | 84.29 | PVsyst report p.2
📉 System Losses
Thermal Loss Factor (W/m²K) | 20
IAM Loss (%) | -3.6 | PVsyst loss diagram
Temperature Loss (%) | -7 | PVsyst loss diagram
Irradiance Level Loss (%) | -0.7 | PVsyst loss diagram
Module Quality Loss (%) | 0.4 | Gain — positive
Module Mismatch Loss (%) | -2 | PVsyst loss diagram
DC Ohmic Wiring Loss (%) | -1 | PVsyst loss diagram
Inverter Loss (%) | -2.6 | PVsyst loss diagram
Night Consumption (%) | -0.1 | PVsyst loss diagram
Source: PVsyst V8.0.20 simulation report — Kömürcüler, Antalya (08/03/2026)